INSTRUCTIONS FOR UPGRADING

IC200UAA007, IC200UAR028, IC200UDD110, IC200UDD120, IC200UDD212, IC200UDR005, IC200UDR006, IC200UDR010, IC200UAL004, IC200UAL005, and IC200UAL006 HARDWARE WITH VERSION 2.00 FIRMWARE

This 2.00 Firmware Upgrade is only compatible with the VersaMax Nano or Micro CPU Models listed above.  DO NOT UPGRADE any other VersaMax Nano or Micro CPU Models with this Upgrade Kit.

The VersaMax Nano and Micro CPUs have operating firmware stored in FLASH memory.  The firmware upgrade and WinLoader update utility for these boards are provided on the upgrade disk. The WinLoader update utility is a Windows-based program that controls downloading the new firmware from the upgrade disk to the FLASH memory on the PLC CPU.  WinLoader requires Windows 95, Windows 98, Windows ME, Windows NT, or Windows 2000.  The hardware required to run these operating systems should suffice to also run WinLoader.

NOTE: The instructions provided outline a specific sequence of procedures that MUST be followed.  If the procedures for some reason are not followed, please contact the GE FANUC hotline for help in setting up the PLC.

- TO INSTALL THE NEW FIRMWARE, PERFORM THE FOLLOWING STEPS:

- Save or backup any programs or data resident in the module before performing the update function.

- Place the PLC in STOP/NOIO Mode.

- Clear the configuration in your PLC.  This will setup the serial ports for 19200 baud, 8 bits per char, odd parity, and 1 stop bit for serial communications.  If they are already set to these default values then this step may not be necessary.

- Clear any faults in the PLC.

- Clear the program in the PLC.

- Clear the references and overrides in the PLC.

- Store the cleared configuration, program, and references to FLASH.

- Close any applications (including PLC programming applications) that may be using the COM ports of your PC.

- Connect the serial port of your computer (master) to port 1 on the PLC to be updated (slave).  (See section at the end of this document for suggested cables to use.)

- Insert the upgrade floppy disk into your A: or B: drive.

- Invoke the WinLoader software package by double clicking on its icon located in drive A: or B: (depending on the drive designation for the 3.5" floppy disk) in Windows Explorer or simply execute it by going to the start menu and selecting RUN.  In the RUN window type A (or B):winloader.exe

- Begin upgrade of firmware by single clicking the "Update" button.  While update is in progress, the OK and RUN LEDs on the PLC will blink in unison, and the status bar on WinLoader will show percentage complete.

- Upon completion of the update a window will "pop up" indicating the status of the update.  If the update was successful, power cycle the PLC and indicate that another device is NOT to be updated by clicking the "No" button.  If not successful, see the "Common Causes of Failure" section below to determine how to correct the problem.

#### COMMMON CAUSES OF FAILURE

- PLC is not in STOP/NOIO mode.  SIDE EFFECTS: A WinLoader dialog box will appear and tell the user that there is a “CPU STATE MISMATCH”.  REMEDY: WinLoader will ask user if it’s OK for WinLoader to clear fault tables and place PLC in STOP/NOIO mode.  Click yes and proceed.

- Connected to wrong serial port.  SIDE EFFECTS: A WinLoader dialog box will appear and tell the user that the “FIRMWARE UPDATE FAILED” and will list several possible reasons why the firmware update failed.  REMEDY: Make sure serial cable is connected to serial port 1 on the PLC and the correct COM port of the PC (should match COM port indicated on WinLoader screen), power-cycle, and start process again.

- COM port on computer already in use.  SIDE EFFECTS: A WinLoader dialog box will appear and tell the user that "FIRMWARE UPDATE FAILED" and that the selected COM port is either busy or does not exist.   REMEDY:  Close any other applications (including PLC programming applications), insure serial cable is connected to correct COM port on the PC and start process again.

# RESTARTING AN INTERRUPTED FIRMWARE UPGRADE

A. Power cycle the PLC.

B. If a partial or erroneous download was performed, the module will power up with the OK and RUN LEDs on the power supply flashing in unison.  If the OK and RUN LEDs are flashing in unison, then begin again at step 6 of the installation instructions, otherwise begin again at step 1.

CABLES REQUIRED FOR UPGRADING

The cable to attach to port 1 of the PLC is sold by GE Fanuc as catalog number IC200CBL500.

If you do not have this cable, any cable that meets the specifications of the wiring diagram in the Serial Port Connections section in Chapter 7, Installation Instructions of the VersaMax Micro PLCs and Nano PLCs Users Manual (GFK-1645A) can be used to connect your PC to port 1 of the PLC.